## Inputs
Input Parameters
Parameter | Unit |  | Value | Notes
Rated Power | VA | S | 44000000
Lagging | - | PF | 0.9
Active Power | VA | P | 39600000
Rated Speed | rpm | n | 187.5
Rated Voltage (line-to-line) | V | V_l | 13800
Frequency | Hz | f | 50 | General assumption due to grid conditions
#Phase | # | m | 3 | General assumption
Magnetic Loading (peak) | T | B_g,peak | 1 | From Table, between 0,85-1,05
Magnetic Loading (avg) | T | B_g,avg | 0.63662
Electric Loading (rms) | A/m | A_rms | 60000 | From Table, between 35000-65000
Electric Loading (peak) | A/m | A_peak | 84852.8137
Current Density (rms) | A/mm2 | J | 4.5 | From Table, between 4-6,5
Specific Machine Constant | kVAs/m3 | C | 401.8968 | First calculated as k_w is equal to 1, after corrected
#Poles | # |  | 32
Pole Pair | # | p | 16
Mech. Frequency | Hz | f_mech | 3.125
Di2L' | m3 |  | 35.0339
Aspect Ratio | - | X | 0.19635 | equal to L'/Di
Axial Length | m | L' | 1.1054
Di | m | D_i | 5.6297
Phase Voltage | V | V_ph | 7967.4337
Area of Poles | m2 | Area_poles | 0.61094
Flux per Pole | Wb | fi_per pole | 0.38894
#Turns per Phase | # | N_per phase | 96.1402 | First calculated as k_w is equal to 1, after corrected
Choosen Turns per Phase | # |  | 96 | Choosen depends on #Turns per Phase
Flux per Pole | Wb | fi_per pole | 0.38951 | Recalculated using Choosen Turns per Phase
Magnetic Loading (avg) | T | B_g,avg | 0.63755 | Recalculated using Choosen Turns per Phase
#Turns | # | N | 288 | Calculated depends on Choosen Turns per Phase
#Slots | # | Q | 288
#Layer | # |  | 2 | General assumption
Slot/Phase/Pole | # | q | 3
Coil Pitch | - |  | 9
Slot Angle | degree | alpha | 20
Coil Pitch | degree | lamda | 180
k_d1 | - |  | 0.9598
k_d3 | - |  | 0.66667
k_d5 | - |  | 0.21757
k_p1 | - |  | 1 | Since we have choosen full-pitch
k_p3 | - |  | -1 | Since we have choosen full-pitch
k_p5 | - |  | 1 | Since we have choosen full-pitch
k_w1 | - |  | 0.9598
k_w3 | - |  | -0.66667
k_w5 | - |  | 0.21757
#Conductors | # |  | 576
Phase Current (rms) | A | I_phase | 1840.8269
Area of Conductors | mm2 | Area_cond | 409.0727
Conductor Area per Slot | mm2 | Area_cond per slot | 818.1453
Stator Yoke Flux Density (peak) | T | B | 1.5 | From Table, between 1,0-1,5
Stator Yoke Flux Density (avg) | T | B | 0.95493
Tooth Flux Density (peak) | T | B | 1.9 | From Table, between 1,6-2,0
Tooth Flux Density (avg) | T | B | 1.2096
Rotor Yoke Flux Density (peak) | T | B | 1.3 | From Table, between 1,0-1,5
Rotor Yoke Flux Density (avg) | T | B | 0.82761
Pole Core Flux Density (peak) | T | B | 1.75 | From Table, between 1,3-1,8
Pole Core Flux Density (avg) | T | B | 1.1141
Tooth Width | mm |  | 32.3686
Slot Pitch | mm |  | 61.4106
Slot Width | mm |  | 29.042
Di/Do | - |  | 0.9 | General Assumption
Do | mm |  | 6255.2342
Pole Pitch | mm |  | 552.6956
Airgap | mm | g | 19.897 | Equation is taken from Lecture Book
Rotor Outer Dia, | mm | d_o | 5589.9167
Stator Yoke Thickness | mm |  | 225.4397
Slot Height | mm |  | 87.322
Slot Area | mm2 |  | 2536.011
Rotor Yoke Thickness | mm |  | 260.1227
Pole Width | mm |  | 316.2872
Fill Factor | - |  | 0.32261
Permeability of Air | H/m | mu_0 | 1.2566e-06
Stator MMF per Pole | A x turns |  | 14311.2148
SCR | - |  | 1.4 | Between 1-1.5 for hydrogenerators
No-Load Field MMF per Pole | A x turns |  | 20035.7008
cos(φ) | - |  | 0.9
sin(φ) | - |  | 0.43589
Full-Load Field MMF per Pole | A x turns |  | 29261.0687
Current Density for Rotor Winding | A/mm2 | J_sth | 3.5 | From Table, between 2-3.5
Fill Factor for Rotor Winding |  |  | 0.5 | General Assumption
Area of Rotor Winding | mm |  | 16720.6107
Area of Empty Space Between Two Poles | mm |  | 33441.2214
di | mm |  | 4500 | It has been choosen considering the shaft and spider connections
Width of Empty Part Next to Pole | mm |  | 176.5743
Total Pole Height | mm |  | 284.8357
Pole Core Height | mm |  | 189.389
Pole Tip Height | mm |  | 95.4467
X_d |  |  | 0.71429
Length of Air in q-Direct | m |  | 0.30473
Area in q-Direct | mm2 |  | 0.19518
R_q |  |  | 1242449.166
L_q | H |  | 0.0074176
Rated Speed (Electrical) | rad/s |  | 314.1593
X_q |  |  | 2.3303
L_d | H |  | 0.0022736
Induced Voltage | V |  | 7967.4337
Mean Length per Turn | mm |  | 3775.1842